4.0	Media Systems

Introduction

This standards section identifies a suggested design approach based on evolving industry standards for voice, data, and video communications as well as wireless transport media, the intention of which is to establish a baseline set of standards for the selection, design, and deployment of common services.

The components discussed in this section are divided into four major groups:

- Twisted copper cable, both indoor and outdoor

- Optical fiber cable, both indoor and outdoor

- Coaxial cable, indoor with only limited references to outdoor cable, and

- Cable distribution, support, and deployment components

Reference to brand names and product types are made in this section and, although identified by manufacturer name and/or description, specific product part or model numbers are not provided due to the evolving and ever changing nature of manufacturer’s product lines and, more specifically, part numbers. In general, the purpose of the herein made recommendations is to ensure consistent deployment of product type as well as installation methods.

A.	Cable Components

The TIA standards place cables into two distinct categories: backbone, and horizontal.  “Backbone cable,” regardless of type, is defined as the cable that connects telecommunications rooms, entrance facilities, and/or equipment rooms between or within buildings.  This definition includes cable formally known as riser and tie cable and outside plant cable.

“Horizontal cable” is the cable between the actual user outlet (known as the work area outlet) and the cross-connect termination.  As a practical matter, the term “horizontal cable” includes the outlet, connector, and cross-connect.  The term “cross-connect” refers to the component(s) enabling cable to be terminated and interconnected or cross-connected to other cables.

In addition to backbone and horizontal cable, this section provides information on cross-connect components, distribution systems, outlet and modular jack hardware, and cable management and support systems.

B.	Copper Cable Systems

Copper cable systems, specifically twisted copper cables, have been in use on the UCSB campus for many years.  Recent changes in the industry, however, have given new life to this medium as a means to meet high-performance telecommunications transmission requirements. The majority of these performance improvements, including both the development of new products and the adoption of higher performance standards, focus on the horizontal cable, also known as “station cable,” connecting user equipment and network transmission equipment.

This subsection defines the minimum recommended configuration for copper cable.  Specifically, it identifies the recommended intra- and inter-building backbone cables and provides criteria for selecting the appropriate horizontal copper cable.

1.	Intra-building Backbone Copper Cable

Intra-building backbone copper cable is typically used for two functions.  First, it is used as a home-run connection path from remote building locations into the entrance facility or equipment room.  This is normally in support of traditional, analog, telephones, as well as other low-voltage applications that need to provide signals to a single, common building location.  The second type of intra-building backbone copper cable is used for higher speed networking, and specifies a cabling system the same as intra-building horizontal copper cabling.  In many cases, terminal rooms are “stacked” and the distance from terminal rooms to the equipment room exceeds the length specifications of the cabling system.  In this case, the cable specifications are specified to allow interconnections between terminal rooms, to allow a “daisy chained’ communication path between remote rooms.

a. The intra-building backbone copper cable connecting a building’s entrance facility or equipment room to individual telecommunications rooms for purposes of home-run communications must be shielded copper sized to meet known or anticipated requirements and installed following BICSI installation guidelines.

The general configuration of these cables should be as follows:

- CMR (riser) rated.

- Bonded, shielded, and air-core style, also known as ARMM type.

- 24 American Wire Gauge (AWG) with staggered twists and a mutual capacitance of not more than 19 nF per 1000 feet.

- The maximum length of the cable is defined by the application and technology to be supported (not subject to the 90 meter limitation).

In buildings that have telecommunications rooms in addition to building equipment/entrance rooms that may also serve as telecommunications rooms, backbone cables must be provided for connection to these additional telecommunications rooms.  These cables should be sized to provide two twisted pair to each potential station outlet location, or three pair for every 125 assignable square feet if the number of outlets cannot be reasonably projected. These dedicated cables are extended from the entrance room directly to  telecommunications room on the same floor or additional floors as may be needed.

It is important to use a properly grounded and shielded cable in the intra-building backbone to lessen the impact of electrical and electronic interference.  These backbone cables often carry both voice and special data circuits and require good installation techniques to reduce the potential for performance problems. Using a shielded cable that is improperly grounded or not grounded at all, actually increases the potential for interference in the cable.  Backbone cables should be grounded at the point of origination and destination in which pairs leave the cable sheath.

b.  The intra-building backbone copper cable connecting terminal rooms to each other, or the equipment room, in support of higher speed networking must meet the following specifications:

- For new buildings and building renovation projects that will be completed on or after January 1, 2010, all installed cable and components must be at least Category 6a.

- For the purpose of identifying an acceptable and cost-effective basic link (i.e., cable, termination hardware, and patch cords) solution that is eligible for an extended manufacturer’s warranty, all components in the horizontal system must be from the same manufacturer.

- All cables will terminate as data cables. Cables shall terminate on rack-mounted modular patch panels identified with the destination terminal or equipment room, as specified in section E4, below..

- All cable jacketing shall be rated for building ceiling conditions; e.g., cable installed in a supply or return air plenum must be plenum rated (CMP).

- All cable systems are to be installed following BICSI, TIA, and manufacturer guidelines with a special emphasis on bend radius, termination methods, and support and bending limitations.

- All copper cable is limited to lengths of not more than 90 meters (295 feet).

- Data jacks are to be RJ-45s wired using the TIA-568B configuration.

- All installed cabling systems must be 100% tested. The permanent link components of the horizontal cabling system must be tested and meet the standards specified.  (Note: we want to look at the language from the E1 IBW contract for this bullet item, so it might change)

- Where possible, patch panels should be mounted in frames designed to support interconnection with active equipment.

- Generally, multiple patch panels of 48 ports or less should be specified rather than single large units to provide greater options for placing and managing patch cords.

- Each patch panel must be placed with a patch cord wire manager directly above and/or below it as outlined in the manufacturer’s installation instructions.

2.	Inter-building Backbone Copper Cable

This subsection has been included in these standards documents to provide requirements in the event copper cabling is the preferred method of distribution for a specific application or service. It should be understood that most UCSB services are extended via optical fiber.

Inter-building backbone copper cable (also known as outside plant [OSP]), like intra-building backbone copper cable is expected to support a variety of voice-grade applications, as well as a range of signal and other low-speed data services.  In addition to stand-alone voice systems, this cable may also need to support point-to-point circuits for signal and control systems, radio and alarm connections, dedicated communication links such as ISDN and T-1 circuits, elevator and emergency telephone, and reporting systems.

With the possibility of  future implementation of Voice Over IP (VoIP) systems which combine multiple applications into a single high-bandwidth network and the increased use of optical fiber for monitoring and security systems, very large copper cable plants are no longer considered a base requirement in today’s environments.  Systems which use fiber as a backbone media may need fewer copper pairs than traditional large centralized systems.  It is necessary to carefully analyze both existing and projected applications and technology to develop an adequate mix of inter-building copper and optical fiber cables.  The current business structure at UCSB would require a stand alone network infrastructure for the implementation of VoIP.

While many applications can now be supported over optical fiber cable, numerous systems designed specifically around twisted copper cable are expected to remain in place, making it necessary to continue to support this medium for a variety of applications.  These copper cables also carry circuits for services such as pay telephones, elevator phones, non-campus telephone services, and other telephone utility lines that may not be directly managed or supported by the campus telecommunications services and therefore may not be included in local documentation.

As suggested most distributed systems use optical fiber to interconnect nodes; however, inter-building copper cable is still the used as method of providing services from the node to the buildings and on to individual users.  This cable is generally available in a variety of configurations from several sources.  Standards for inter-building backbone copper cable are as follows:

- 24 AWG should be used for cable runs up to 2,500 feet, and 22 AWG for longer distances.

- Plastic-Insulated Conductor (PIC) cable with color-coded 25-pair binder groups protected by a shield and heavy outer cover should be used in all outdoor locations.

- All cables placed in an outdoor environment must be constructed with water-exclusion gel, even if only a portion of the cable may be exposed to moisture.

- The use of aerial cable is not recommended nor supported under these Standards.

The selection of cable construction and sheath type is driven by the environment in which the cable will be installed.  Generally, outdoor backbone cable is not placed in a hazardous environment; it is contained within conduit.

The greatest threats to the long-term life of outdoor cables are damage caused during its placement, accidental physical damage during building construction or during the placement of other utilities, and moisture.  Using a water-exclusion gel-filled cable will significantly reduce problems with moisture during the life of the cable.  Selecting the appropriate cable sheath and overall construction can limit damage during placement, while proper pathway design and cable installation can address ongoing physical damage concerns.

Figure 4-1 outlines the major recommended cable types following the nomenclature generally accepted within the industry.  In addition, the Rural Utility Service (RUS), formally the Rural Electrification Authority (REA), is referenced as a standard, and an acceptable product is identified.

| BACKBONE COPPER CABLE CONSTRUCTION |
| --- |
| Sheath Type | Major Components | Primary Uses w/Comments |
| Filled ASP | Aluminum, steel & polyethylene | Direct buried & conduit (Offers greater mechanical protection) |
| Filled Alpeth | Aluminum & polyethylene | Conduit & tunnel (Good general use cable design) |
| RUS PE 39 | Aluminum & polyethylene | Conduit & tunnel (Good general use cable design) |

Figure 4-1

Copper Cable Sheaths

Backbone copper cables are available in a variety of configurations in sizes from 12 to 4,200 pairs.  The largest size cable generally utilized in a four-inch conduit is 1,200 pair (assuming a standard bonded sheath, 24 gauge, ASP cable).  There are cables on the market that allow 1,800 or more pairs to be installed in a four-inch conduit, but for planning purposes, it is best to assume a maximum of 1,200 pairs per four-inch conduit.  Large cables are generally available in relatively short lengths (500 to 750 feet).  These short lengths must be taken into consideration when planning new infrastructure facilities to ensure that pathway distances do not exceed the available products

a.	Cable Sizing

Determining the number of pairs required to serve a building is a straightforward process if there is supported data for current and future load (number of users) in the facility.  When assuming the greatest use of copper cable in a building will be used to support voice telephone service, it is reasonable to use one-and-one-half to two pairs per work area outlet (or telephone) as the maximum number of pairs required to support the majority of telephone systems on the market today.  The designer must determine the projected number of users (and potential user areas) and the number of miscellaneous pairs needed for “special” circuits to determine a starting point for the sizing process.

If the number of current and potential users is not known, cables should be sized to provide 1.5 to 2 pair for every 125 assignable square feet in a building as a starting point.  From there, the designer should add pairs for known applications, such as monitoring and control equipment, security systems, and electronic key access.  Once a total number of pairs has been determined, the designer should assume no more than 85% of the pairs will be usable over the life of the cable and round up to be nearest generally recommended and available cable size; 100, 200, 300, 400, 600, 900 or 1,200 pairs.

It is important that the designer focus on developing a reasonable forecast for each building and, as needed, each floor of each building.  Obviously, the best manner in which to develop a cable design is to fully understand the needs of the users and the potential applications to be supported.  While installing sufficient cable to meet only an initially defined application will result in too few pairs for the long-term use of most facilities, installing the maximum pair count into every building is expensive and unnecessary.  The designer must factor in the range of applications and needs that are likely to require support over the useful life of the installed cable, not the building.  Installation of new cable, perhaps even a new medium, can be expected over the building’s useful life span.

BACKBONE COPPER CABLE SIZING EXAMPLE 20,000 Assigned Square Feet (ASF)

20,000 / 125 = 160 work areas (ASF divided by work area size)

160 x 1.5 = 240 pairs (Work area times average pair usage)

40 pairs for miscellaneous services (Known or assumed figure)

240 + 40 = 280 pairs (Sub total of actual pairs required)

280 / .85 = 329 pairs (Cable life allowance for problem pairs)

Increase to the next highest cable pair size - Install a 400 pair cable

Figure 4-2

Copper Cable Sizing

If the designer focuses only on an assignable square foot algorithm, specialty facilities, such as libraries, sports complexes, and performance centers, would end up with backbone copper cables of enormous size with very little actual requirement.  Conversely, a small building may house a help desk application or a registration call center that requires a significantly higher work area density than the assumed 125 square feet.  It is up to the designer to obtain or develop the information that will result in an accurate, or at least a reasonable, forecast.

b.	Copper Cable Protection

Cable protectors are used in conjunction with proper bonding and grounding to provide electrical hazard protection to human life and sensitive electronic equipment.  The decision of where and how to use protectors is not clear-cut and must be viewed as part of an overall cable design process.  Generally, copper cables serving on-campus switching systems should be protected at least at the switch end.  The decision to protect the station end (other buildings) is based on campus layout, potential for lightning strikes or power faults, and historical electrical fault problems.

In general, small buildings that are very close to one another and are grouped around a larger one are protected from lightning strikes because of the umbrella effect of the large, closely placed buildings.  In such a case, only selected buildings need protectors.  However, if there is a history of electrical problems, all buildings should be protected.

Conversely, a campus that has buildings widely spaced and a history of lightning-related problems must protect all buildings.  The "rules-of-thumb" for protecting copper cables entering a building are as follows:

- If a building is located on the other side of a roadway and/or is remote from the main part of campus, it must be protected.

- If any part of the serving copper cable is above ground (on poles), it must be protected.

- If any part of the serving cable is exposed (placed near) high voltage power cables, it must be protected.

- If there is a history of power fault problems and/or lightning strikes, the cable must be protected.

There are two primary types of protector panels.  The first consists of the protector field and an integrated cross-connect terminal.  This product, such as the 188 unit, is most often used on smaller pair count cables, such as in installations of less than 900 pair. This type of product allows cross connect wires to be interconnected with riser or station cable without other components.

The Main Cross-connect (MC) cable terminations and any building with 25 or more pair should be served by wall- or rack-mounted protectors that are separate from the cross connect terminals.  These large pair count configurations provide connection points for multi-pair testing, and the separate cross-connect fields can be incorporated into high density systems.

Any facility that requires termination of more than 900 pairs must be specifically designed using methods applicable to main distribution frames and central offices.  Many of the equipment manufacturers have expertise available in-house to assist in developing a detailed and long-term plan for meeting the needs of large copper cable protection and termination installations.

Both types of protector panels use the same type of protectors (1 protector unit per cable pair).  The recommended unit is a fast-acting, 3 element (5 pin) gas-tube unit with sneak current (low voltages) protection.  All copper cable pairs placed into a facility must be equipped with protectors, not simply the ones expected to be activated in the near term.

c.	Splice Cases

All splices must be contained within a splice case.  All outdoor (vault) splice cases should be encapsulated, re-enterable units fully dressed and enclosed to fit the number and type of cables terminated.  All end plates must be designed for the number and size of cables served by the splice case and designed to seal around each cable individually.

The designer must select and specify an appropriate splice case when installing copper cable systems.  Individual splice cases are designed for specific environments, including use in vaults, underground burial, use within a building, or mounted on a pole.  Inferior products, inadequate installation techniques, or incorrect use of a particular product can lead to moisture leaks and ultimately cable failures.

All filled cable must be connected to air core cable within a sealed splice case prior to termination of entry pairs.  In no case shall a filled cable be directly terminated on a backboard.  All entrance cables must utilize a splice case rated (by the NEC) for use in those situations.

Outdoor vault splice cases should be stainless steel or heavy neoprene.  Indoor cases used to terminate inter-building cable filled with water-exclusion gel must also be capable of completely sealing around all cables at each end of the case and must be rated to contain a filled entrance splice.  Splices of 25 or more pairs must utilize splice modules for connecting cable pairs.  Cable shields must be bonded through all splices and must be grounded as soon as possible upon entering a building or on any floor in which pairs leave the sheath on riser cables.

3.	Intra-building Horizontal Copper Cable

Intra-building horizontal unshielded twisted pair (UTP) copper cable, also known as station cable, is the portion of the infrastructure that is changing the most rapidly.  In an effort to keep up with the transmission performance requirements of high-speed data and image applications, this medium and its associated components continue to undergo significant changes.

Although this standards document’s main focus deals with infrastructure that supports traditional desktop voice dial tone, data networking and some video, it nonetheless has been  positioned to support a variety of other emerging technologies.  Some of these technologies include:

- Voice over Internet Protocol (VoIP), which is anticipated to replace traditional digital telephone (PBX) systems, thus rendering legacy voice cabling systems virtually useless other than support of analog services.

- Internet Protocol (IP) based video, which will support closed circuit television (CCTV) security cameras traditionally wired with coaxial cable.

- Broadband CATV video distribution over short distances, again replacing coaxial cable.

- IP-based Building Automation System (BAS) devices supporting secured access, heating, lighting, ventilation and other automated environmental systems, eliminating expensive and non-standard proprietary cable systems.

Currently, the UCSB data network desktop throughput standard is 10/100 Mbps with backbone throughput of 1 Gbps.  Desktop throughputs of 10/100 Mbps - at a distance of up to 100 meters - are currently supported by horizontal Cat 5e and Cat 6 cable.  Nonetheless, with either Cat 5e or Cat 6 cable, UCSB will be well positioned to increase desktop throughput to 1 Gbps and likewise herein identified singlemode fiber optic cable will be capable of supporting minimum 10 Gbps in the backbone.

Additionally, it is not the intent of these standards to direct the replacement of the installed base of properly installed data category 5e or even cat 5 cables with new cat 6 or higher grade cable types.  These standards identify Cat 6a cables, as well as associated components to be installed in retrofit projects for data purposes when authorized UCSB Planning, Communications Services, and  IT staff determine it will be necessary.

The recommended standard for horizontal (workstation wiring) copper cable systems is as follows:

- For new buildings and building renovation projects that will be completed prior to January 1, 2015, all installed horizontal cable and components should be at least Category 5e.

- For new buildings and building renovation projects that will be completed on or after January 1, 2015, all installed horizontal cable and components must be at least Category 6a.

- For the purpose of identifying an acceptable and cost-effective basic link (i.e., cable, termination hardware, and patch cords) solution that is eligible for an extended manufacturer’s warranty, all components in the horizontal system must be from the same manufacturer.

- Standard communications outlets will be served by three (3) high speed, four-pair, 100 ohm, twisted pair copper cables.

- One (1) cable will terminate as a voice cable and two (2) cables will terminate as data cables. Voice cable terminations shall terminate on rack mounted patch panels identified with a “V” and Data cable terminations shall terminate on rack-mounted modular patch panels identified with a “D1” or “D2”.

- All horizontal cable jacketing shall be rated for building ceiling conditions; e.g., cable installed in a supply or return air plenum must be plenum rated (CMP).

- All cable systems are to be installed following BICSI, TIA, and manufacturer guidelines with a special emphasis on bend radius, termination methods, and support and bending limitations.

- All horizontal copper cable is limited to lengths of not more than 90 meters (295 feet).

- All installed cabling systems must be 100% tested. The permanent link components of the horizontal cabling system must be tested and meet the standards specified. .  (Note: we want to look at the language from the E1 IBW contract for this bullet item, so it might change)

- Voice and data jacks are to be RJ-45s wired using the TIA-568B configuration.

a.	Work Area Outlet

Minimum standards for work area outlets are as follows:

- Standard work area outlets should include a multi-position jack faceplate and three (3) 4-pair copper cables.

- Outlet boxes should be 4 11/16 inches square by 2 1/8  inches deep, with a 1 ¼” inch knockout.

- Outlet boxes should be fitted with 1 1/4” conduit stubbed into the nearest open ceiling area, nearest cable tray or routed back to the closest Telecommunications Room.

- Outlet boxes that support single-gang faceplates shall typically be fitted with single-gang rings.

- Outlet boxes that will support double-gang faceplates shall be fitted with double-gang rings.

- Faceplates shall provide a surface suitable for placing an identifying mark next to each jack or connector, not simply a single identifier for the faceplate. These labels shall be placed in the provided faceplate label holders and on the top edge of the faceplate so as to allow for direct above viewing.

- Connectors for fiber and/or coaxial cable should be recessed or angled in the faceplate to reduce the potential for physical damage.

A significant issue with work area outlets and horizontal cable within administration buildings is the use of modular furniture.  Much of the modular furniture available today is either designed to support, or has optional raceways to support, high-speed telecommunication cable.  Unfortunately, many installations do not take into consideration the need to link the modular furniture to the distribution system.

Modular furniture needs to be designed with a specific telecommunications interconnection in mind rather than simply assuming that a connection method similar to the electrical service will be used.  For example, a single floor outlet box will often be sufficient to serve only two user locations due to the size of the feeding conduit and the number and type of cables to be installed.  Without proper planning, this situation may be overlooked, and modular furniture designed to seat four or even eight people will be linked to the horizontal distribution system by only a single poke-through floor appliance or a single ¾ inch flexible whip to a wall box.  Horizontal pathway and cabling must be specifically designed from the telecommunications room to and through the furniture interconnection point and raceway system to the user’s work area outlet. Typical pathway solutions for modular furniture include: floor boxes, wall feeds and/or communications poles.

In general, wiring a room specifically for modular furniture is to be discouraged.  If done, there should NOT be a conduit stub-out, but rather a dual-gang box where the furniture will connect.  This allows the box to be used as a wallplate by some future occupant. In consideration of the higher densities needed for modular furniture, the design should try to distribute the wiring to multiple locations, not centralize the connections. The drop length might be longer when using modular furniture, so the 10m path cord allowance needs to be adjusted.  Don't measure the 90m from patch panel to outlet box, but rather, include the length planned inside the furniture as part of the distance drop length.  For planning purposes, the following table identifies minimum pathway requirements for modular furniture installations:

|  | Floor Poke Through | Wall Feed | Communications Poll Feed |
| --- | --- | --- | --- |
| Two Modular Workstations | Single 1 ½” Conduit | Single 1 ½” Conduit | 2” X 2” dedicated channel |
| Four Modular Workstations | Single 2” Conduit | One 2” Conduits | 2” X 4” dedicated channel |
| Six Modular Workstations | Two 1 ½” Conduits, One for every (3) Workstations | Two 1 ½” Conduits | 4” X 4” dedicated channel |
| Eight Modular Workstations | Two 2” Conduits, One for every (4) Workstations | Two 2” Conduits | Two 4” X 4” dedicated channel |

Figure 4-3

Minimum Conduit requirements for Modular Furniture configurations.

b.	Cross-Connect Hardware

The cross-connect is the point at which horizontal cables link to backbone cables or network equipment.  Typically in a telecommunications room, voice circuits will be interconnected with cross-connect or hook-up wire to backbone cables extending to a voice switching node or central switch site.  Data circuits typically interconnect with patch cords to network equipment within the telecommunications room.

Recommendations for terminating voice-grade services are as follows:

- On insulation displacement connector (IDC) terminal such as 110 type wiring blocks or panels.

- Cable slack must be provided above the work area outlet and above the telecommunications room termination to allow rearrangement of cable within a five foot radius.

- IDC terminals may be wall- or frame-mounted and must be equipped with wire raceways designed to support the placement and maintenance of cross-connect or hook-up wire.

- In configurations above 3,600 pair (such as in the MC or in an equipment room with a switching node), a detailed plan for jumper placement must be developed.

- Wall-mounted terminals should generally be placed from left-to-right on a wall, with station cable above the cross-connect wire holder and riser cable below.

Recommendations for terminating horizontal data cable are as follows:

- All voice and data station cable should be terminated to separately identified modular patch panels consistent with the grade of cable being installed.

- Where possible, patch panels should be mounted in frames designed to support interconnection with active equipment.

- Generally, multiple patch panels of 48 ports or less should be specified rather than single large units to provide greater options for placing and managing patch cords.

- The accepted patch panel layout shall be as follows:

  - The first patch panel mounted in the rack shall be designated as a Voice panel.

  - The second patch panel shall be designated as Data – 1.

  - The third patch panel shall be designated as Data – 2.

- If additional workstation cabling is required, three additional patch panels must be installed with the same designations.

- Each patch panel must be placed with a patch cord wire manager directly above and/or below it as outlined in the manufacturer’s installation instructions.

- Each group of patch panels must have additional wireways mounted to support the use of multiple patch cords.  We are unclear what this bullet point means ????

4.	Work Area Termination

The UCSB standard is for the termination of the four-pair station cables in separate 8-position modular jacks (RJ45).  Station cable should not be split, i.e., terminated on two separate jacks, to routinely meet multiple service needs.  Any design that requires the horizontal cable to be terminated more than once will lead to performance difficulties over time, and different configurations of this type are very difficult to maintain over the life of the system.  If two jacks are required and it is not possible to install a separate cable, an external splitter consisting of a single male jack and two or more female units should be installed.

C.	Fiber Optic Cable Systems

Optical fiber cable is classified into two major categories: singlemode, and multimode.  These designations refer to the number of paths light can take in each type of fiber.  A smaller number of paths assures lower modal dispersion, and greater effective bandwidth.The number of modes is determined by several factors, including the physical size of the fiber.  While many of the fibers have a 125 µm overall size, the inner core within which the light travels varies in size.  The major fiber core sizes are identified below:

- 7 to 10 µm core diameter singlemode fiber is used for broadband (e.g., CATV) and long distance systems. Singlemode fibers use laser light sources, and the cable has a wide bandwidth that supports high-quality connections at high data rates.

- 62.5 µm core diameter multimode fiber is the standard core size previously installed within the UCSB campus.  UCSB will continue to install 62.5 µm only where it must interface directly with installed legacy systems.

- 50 µm core diameter multimode fiber is the standard core size to be used for all new installations on the UCSB campus.

- If a required connection, supporting 1000BASE SX, has a distance greater than 220 meters, a singe mode fiber optic cable is recommended.

- Terminated fiber optic cabling systems require testing to be accepted.  Table 4-4 shows typical cable types, uses, and allowable lengths and attenuation.  All cables should be tested at the wavelengths used on those cables (i.e. 850nm and 1300nm for multimode cables). The testing should include the maximum date rate standard for that cable (i.e. 10Gbps for 50u multimode, 1Gbps for 62.5u multimode, etc.)

1.	Multimode Fiber Cable

One factor that must be considered is the length of the average transmission link factored into the equation of signal requirements.  Most UCSB buildings have cable lengths within a building of less than 220 meters, even assuming each cable is home run from the work area outlet to a central equipment room. 50/125 µm OM3 cable is used to support 1000BASE-SX (Gigabit Ethernet using the less expensive LED transmitter) for distances up to 1000 meters.

The recommendation of these Standards is to install 50/125 µm OM3 multimode fiber within buildings on all new projects.  At this time, there is no reason to replace existing 62.5/125 cable with the 50 µm product.

|  | Wave | Maximum Distance (Meters) | Allowable Attenuation |
| --- | --- | --- | --- |
| Application | Length nm | 62.5/125um | 62.5/125um |
| 10BASE-FL | 850 | 2000 | 12.5dB |
| 10BASE-FX | 1300 | 2000 | 11dB |
| FDDI | 1300 | 2000 | 11dB |
| ATM 52MB 155MB 622MB | 1300 1300 1300 | 3000 2000 500 | 10dB 10dB 6dB |
| 1000BASESX | 850 | 220 | 3.2dB |
| 1000BASELX | 1300 | 550 | 4dB |

This table needs to include information on 100FX links and 10Gbps links, and provide distance and attenuation data for 50/125 um OM3 fiber

Figure 4-4

Multimode Fiber Optic Cable Performance Criteria

2.	Connectors & Couplers

There are two general groups of fiber optic connectors on the market today: traditional-sized and small form factor (SFF) connectors.  Some traditional fiber optic connectors include the SC, ST, FC, Biconic and SMA.  Of these, SC and ST connectors are most commonly found on the UCSB campus.  There are few reasons to change an existing connector that is functioning correctly.  Jumper cables can be fabricated with different connectors on each end to allow linking dissimilar components.

Small form factor connectors offer a greatly reduced footprint, similar in size to the RJ45 copper cable jack.  Various types of SFF connectors, e.g., MT-RJ, LC, VF45, and the Opti-jack have been developed.  Each is supported by one or more manufacturers.  Although the revised TIA specification included support of SFF connectors, it stopped short of endorsing one type of connector over the others.  The standard provides several performance characteristics that a connector must meet, allowing users to choose an individual product.  At this time, the most often used SFF connector is the LC.

The prime benefits of the SFF connectors are that it allows the installation of twice the number of connections within the same space as traditional connectors, and it can be terminated for less cost.  The downsides are questions regarding reliability, performance, and durability.  These issues are in addition to the basic question of whether the fiber terminal panels should be twice as densely populated as they are currently causing even more congestion for patch cord management.

The fiber optic connector type recommended for use on all 62.5 um multimode backbone cabling shall be “ST” type as defined in the TIA-568 standards. This conforms with the legacy connector type used throughout campus for this cable type.  The connector (beige) should be used for all 62.5 um multimode cable strands.  The fiber optic connector type recommended for use on all 50 um multimode backbone cabling shall be “LC” type.  This gives network personnel the ability to determine fiber type based on its termination.  The fiber optic connector type recommended for use on all singlemode backbone cabling shall be “SC” type as defined in TIA-568 standards. The connector (blue) should be used for all singlemode cable strands. It is important that all fiber optic cables use an ultra polished connector (UPC) with factory-made pigtails fusion-spliced to the backbone cable to reduce signal reflectance. This requirement is extremely important to maintain adequate signal levels when extending the network fiber ring to a new building.

The most significant problem with wideband optical fiber (especially video) systems on campuses are not loss, but too much reflected signal.  Normal connectors provide a return loss measurement or reflectance in the area of -26 dB for singlemode fiber.  The target for broadband video and some proposed multi-gigabit data systems is -55 dB (the higher the number the better).  Experience with a variety of CATV system on various campuses indicates that poor return loss is the central problem with most newly installed systems.  Fiber that does not meet the return loss measurements generally degrades the video signal or in some cases makes it completely unusable.  By routinely installing factory-made APC connectors on all singlemode backbone cable, and specifically to use “FC” style pigtail assemblies for AM video systems, the designer has a greater chance of meeting both today’s and tomorrow’s transmission requirements.

3.	Fiber Optic Patch Panels

For fiber hubs or distribution locations supporting multiple fiber optic cables that distribute to smaller buildings, 72-port, rack-mounted, fiber optic patch panels should be used.  For those smaller buildings where fiber counts typically range from 12 to 24 optical cable strands, 24-port, rack-mounted, fiber optic patch panels should be used.  Patch panels shall include appropriate connector panels that support anywhere from 6 to as many as 24 connectors.

Small wall-mounted 12- to 24-port fiber optic panels should not be used except to terminate a very limited number of fiber optic strands in locations where space is limited or further growth is unlikely.  Whenever possible, existing small wall-mount units should be removed and the fibers consolidated into 24-port rack-mount patch panels.  If a room does not offer sufficient space for a floor-mounted rack, wall-mounted racks can be installed.  In problem locations where there is no room for wall-mount racks, wall-mount fiber optic panels, as previously stated, should remain or be installed.

50 um multimode fiber optic strands shall be spliced with LC pigtails, and singlemode strands spliced with SC pigtails.  Backbone cables and horizontal cables should be housed in separate patch panels, or at minimum, separate connector panels.

Jumper cable management becomes a critical component on large fiber installations.  All patch panel designs must include both vertical and horizontal wire managers designed specifically to route cables from panels, through the frames, to equipment or other panels.  The design must also make allowances for storage of cable slack in such a manner as to protect the cable without restricting access to it for ongoing maintenance.

4.	Inter-building Backbone Fiber Cable

Each campus building should be connected to the main campus network ring at two locations with both multimode and singlemode optical fibers.  There are three overall design concepts for fiber distribution:

- A distribution ring (used on the main campus) approach in which fibers extend out in two directions from each building to the network.

- A central hub approach in which all fibers radiate from one central space, such as the MC, to each building on campus.

- A distributed node approach in which fibers extend from individual buildings to a concentration point or node location.  Each node is then connected to a central point, such as the MDF.

In all cases, the facilities must be designed to support both point-to-point systems and point-to-multipoint, or loop or “ring”, systems.  This is generally accomplished by installing sufficient cable and by providing adequate support hardware such as splice trays and patch panels. The node approach also allows specific systems to be installed in a ring manner, providing a fault-tolerant design and allowing a properly configured system to continue to function in the event of a break in the fiber ring.

The run size figures shown in Figure 4-5 are minimum recommendations to be used whenever actual campus requirements are not known or cannot be reasonably defined.  Common sense must play a role in sizing these cables, and there will be cases in which other configurations should be used.  For example, individual buildings or facilities without networking requirements typically do not need fiber optic cable.  On the other hand, a central computing resource or a video headend re-transmission facility will likely require strand counts in excess of those recommended in this standards document. An additional multimode cable may be required to support buildings isolated due to presence of the new building.  Insertions must be compatible with the existing cable plant, and sized at least as large as the existing cable count to adjacent buildings.

| Building Type | Singlemode |
| --- | --- |
| Small – less than 10,000 sq. ft. | 24 |
| Large – greater than 10,000 sq. ft. | 60 |

Figure 4-5

Minimum Fiber Cable Strand Counts

Each building should contain an additional 40-foot section of each optical fiber cable, neatly coiled in a maintenance loop (figure eight) and secured before reaching the final termination point, which can be utilized as splicing slack in the event of a cable break.  When placed within a conduit, fiber optic cable should be installed within an orange, one-inch innerduct.  Within a building, the use of innerduct is required only if there is a concern the cable is susceptible to damage or may be mistaken for another medium.  When innerduct is installed within a building, like cable, it must be properly rated for building interior conditions.

There are different types of backbone cable construction suitable for use on campus.  Generally, outdoor cables should be:

- Water exclusion gel-filled, dielectric, loose tube construction with a tensile strength of 600 lbs. (long term).

Specialized indoor-outdoor backbone (riser) cables, that are NEC rated, are available and are constructed of materials suitable for use both inter- (between) and intra- (within) building applications.  The use of these cables can eliminate a splice point in the cable and reduce the cost of installation.

An important point to remember when planning an inter-building fiber optic backbone system is to limit the number of splices, especially outdoor splices.  By keeping splice locations within buildings, where they can be protected and, as necessary, accessed by authorized personnel, the fiber design will provide a great deal of flexibility without the high cost of dedicated cable runs to every building.

5.	Intra-building Backbone Fiber Cable

Both multimode and singlemode fiber optic cable should be installed in between building entrance/equipment rooms and telecommunications (riser) rooms.  At a minimum, the backbone optical fiber cables should consist of (12) multimode and twelve (12) singlemode fibers to each telecommunications room from a fiber hub location in a building's equipment or entrance facilities.  These cables should be "home-run" directly from the equipment rooms into the individual telecommunications rooms on one or more floors.  All fiber cables should be contained within innerduct if any potential for physical damage exists. All cable should be clearly marked as optical cables for additional physical protection.

| Fiber Cable Type | Wavelength (nms) | Maximum Attenuation (dB/km) |
| --- | --- | --- |
| 50/125 um OM3 Multimode | 850 1300 | 3.5 1.5 |
| 9/125um Singlemode | 1310 1550 | 1.0 1.0 |

Figure 4-6

Optical Fiber Performance Parameters

All intra-building fiber backbone cables must be properly rated for building conditions (e.g., OFNR, OFNP)  tight buffered, fan-out cables with a dielectric central member and must carry a crush resistance rating of at least 1100 lbs. per inch.  Cables must have a 900 µm buffer and must meet the performance characteristics as defined in ANSI/ICEA S-83-596:

D.	Coaxial Cable Systems

Coaxial cable systems are increasingly less deployed as part of today’s video distribution systems in a campus environment; nonetheless, these systems still play an important role in the distribution of multi-channel video programming.  General information regarding coaxial cable is included in this Standard; however, it is for general information purposes only. With the shift of digital imaging and alternative methods of transmitting video and audio signals, the decision on how or when to implement coaxial cable or an alternative is up to individual campus planners.

Coaxial cables are still used for a variety of services (e.g., terrestrial cable TV, satellite TV, closed circuit television TV, security, etc.).  Each of these systems requires unique cable systems and equipment engineered to meet specific requirements and more in-depth information regarding these systems is beyond the scope of this Standard.  This document assumes that the most frequent use of coaxial cable is the distribution of multi-channel video signals (using cable television technologies) within campus buildings.

Although these standards recognize there are a variety of technical alternatives for distributing multi-channel broadband television signals, the design concept of these Standards focuses on a hybrid fiber/coax solution, which, in general terms, is as follows:

- Signal outputs from local service providers, campus programming, satellite feeds, and other sources are balanced and combined into a common feed for a fiber optic-based analog cable television transmission system consisting of one or more laser transmitters;

- The output of the transmitters is fed into optical splitters either at a single headend location or in a multiple node arrangement;

- Each optical splitter, such as a two, four or eight-port unit, is constructed to provide a specific level of signal loss and is connected to a backbone singlemode fiber optic cable feeding an individual building;

- Each building is equipped with a fiber receiver that accepts the incoming fiber-based signal and converts it to a broadband radio frequency (RF) signal;

- The RF signal is fed into a standard coaxial cable based RF distribution system consisting of active and passive components (e.g., amplifiers, splitters, couplers, multiport taps, etc.); and

- The RF system is distributed in most buildings by using singlemode or multimode distribution systems or with 75 ohm half-inch (.500) and/or RG11 coaxial backbone cable and RG6 horizontal station cable.

The actual design of any television distribution system is beyond the scope of this document and should be undertaken only by a qualified video design engineer.  However, the CATV distribution system, including all active and passive devices, is considered a basic component of a campus telecommunications infrastructure and must be strategically engineered into any infrastructure design.  This includes all components from the work area outlet (not television sets) back to the headend transmission system.

The primary components of the system are:

- Headend signal processing equipment necessary to bring all signals to a common level;

- Combiners, splitters, and couplers necessary to present the signal to the distribution system;

- 860 MHz (minimum 103 channels) analog DBF laser transmission system;

- Optical receivers;

- Angled Physical Contact (APC) optical fiber connectors on all serving, distribution, and jumper cables;

- 1 GHz active RF components such as amplifiers and equalizers;

- 1 GHz passive RF components such as splitters, directional couplers, multiport taps, terminators, attenuators, etc.;

- Backbone .500 coaxial cable extended floor-to-floor

- Horizontal RG6 (drop) cable; and

- Work area faceplates and connectors.

The distributing system must be designed to average 3 dB or more to every station location.  The multiport taps should be designed with no more than half of the taps used in the initial design.  Additional taps must be provided throughout each floor of each building to allow for growth without redesigning the distribution system.

Video that originates in a classroom or other facility can be economically transmitted back to the campus headend for storage or retransmission by using low cost multimode fiber optic transmitters.  There are several units on the market that include one or more quality audio channels and a “broadcast quality” video signal over the same fiber.

E.	Labeling

#### The purpose of this section is to establish generic guidelines for uniform labeling of telecommunications cable systems in a Class 3 campus environment.  It is anticipated that these guidelines will be used by the architect, designer, consultants, contractors, installers, and facility administrators involved with the administration of the telecommunications infrastructure.  Physical labeling of telecommunications cable systems and related components shall be, whenever practical, in conformance with this document and TIA-606 Administration Standards.  Components shall include, but are not limited to, the following:

##### Buildings

##### Telecommunications Spaces

##### Cables (both ends)

##### Faceplates

##### Wiring blocks

##### Patch panels

#### Miscellaneous other components

#### All cables and related components shall be permanently marked with machine-generated insert, adhesive, and wrap around (self-laminating) labels.

#### 1.	Label Format

#### Both ends of all cables shall be uniquely and permanently marked with machine-generated or stenciled (not handwritten) labels, according to current practice and as approved by UCSB before installation.

#### Label faceplates with adhesive machine generated labels.

##### All labels shall be computer or machine generated, no hand written labeling unless otherwise noted.

##### All label fields shall be separated by a hyphen.

##### Label type size shall be 12 point, unless space is not available.

### 2.	Building

A unique identifier is assigned by campus for each building using one numeric identifiers.

Example: 614, 572, 384, etc.

### 3.	Telecommunications Spaces

#### Telecommunications spaces (e.g., EF, MC, Equipment Rooms, Server Rooms, Telecommunications Rooms, etc.) shall be assigned unique identifiers based on room number and location.  This is important where two telecommunication spaces may share the same campus room designation but be physically separated by a large distance.

#### Example for a 1st floor EF/MC might be: 112.  A set of second floor telecommunications rooms sharing a common room number might be designated 2020W and 2020E for the west and east locations, respectively.

4.	Campus Backbone

A unique backbone cable identifier shall be assigned to each inter-building backbone cable connecting building telecommunications spaces in different buildings.

- The first field shall identify originating building, e.g., “51”. (Backbone cable will always terminate in the EF so this space is not identified.)

- The second field shall identify destination building, e.g. “23”.

- The third field shall identify the cable using a one or two character numeric identifier, e.g., “1” (Keep in mind there can be more than one of the same type and size of cable therefore each cable needs an individual number.)

- The fourth field shall identify copper C or fiber F.

- The fifth field shall identify copper pair count (e.g., 900 pairs) or fiber strand count (e.g., 144 strands).

- Each label shall start with the originating building and fields shall be separated by a hyphen.

Copper cable example: 51-23-1-C-900 and 23-51-1-C-900

Fiber cable example: 51-23-1-F-144 and 23-51-1-F-144

#### 5.	Building Backbone

A unique backbone cable identifier shall be assigned to each intra-building backbone cable connecting building telecommunications spaces in the same building.  The first and second fields should explicitly call out the type of space, based on the letter designations of “EF” for entrance facility, “ER” for equipment room, “TR” for telecommunications room, or “MR” for machine room.

- The first field shall identify originating telecommunications space: e.g., TR112

- The second field shall identify destination telecommunications space, e.g. MR212

- The third field shall identify the cable using a one character numeric identifier, e.g., 1

- The fourth field shall identify copper C or fiber F.

- The fifth field shall identify copper pair (e.g., 100-pairs) or fiber strand count (e.g., 24 stands).

- Each label shall start with the originating building and fields shall be separated by a hyphen.

Copper cable example: TR#112-TR#212-1-C-100 and TR#212-TR#112-C-100

Fiber cable example: TR#112-TR#212-1-F-24 and TR#212-TR#112-F-24

#### 6.	Horizontal Station Cables

##### The first field shall identify the service type, V for voice, D1 or D2 for data.

##### The second field shall identify three numbers for each station cable, e.g., 011

##### Example for a voice cable: V-011

##### Example for a data cable: D1-011

#### 7.	Faceplates

##### The first field shall identify the building number for this location.  Example: 672

##### The second field shall identify the location of the telecommunication space where this wiring terminates. Example: TR2020E

##### The third field will be the three numbers for each work area outlet, e.g., 011

##### There shall be a series of letters and numbers representing the individual ports for each faceplate.

##### Example for a three cable faceplate: 011, V, D1, & D2

672-TR2020E-011 672-TR2020E-011 V D1 D2

- Note that port density issues may require creative modifications from the example shown.  For instance, the building and telecommunications room information may be marked on the outside of a grouping of wallplates, with each jack labeled with the station ID and “V”, “D1” or “D2” to identify them.  It is important that the entire identifier can be clearly understood for each termination.

- 8.	Patch Panels

- Within each group of three patch panels, the panel itself will be clearly labeled with a “V”, “D1” or “D2” to identify which jack in the wallplates are associated with this panel.

- The patch panel ports will be numbered sequentially with the station ID over all the panels present (i.e. don’t start over everytime you have a new 24-port panel)

- Each patch panel port will be labeled with  a room number allocation

Example: 2312-011

9.	Wiring Blocks

  - All wiring block designation strips shall be labeled and color-coded with their appropriate field colors according to TIA - 606 8.3.2, Color Coding Rules.

  - Backbone Cable Wiring Blocks

      - Cable pairs shall be identified in 25-pair increments or binder groups.  Each designation strip shall start with the beginning pair at the far left and ending pair at the far right.

Example for a 100-pair cable:

0 25

26 50

51 75

76 100

  - Station Cable Wiring Blocks

##### The first field shall identify the room number, e.g., 134

##### Each designation strip shall be labeled with as many as six station cables.

Example for six 4-pair:

| 134 | 136 | 145 | 146 | 147 | 151 |
| --- | --- | --- | --- | --- | --- |

F.	Wireless Systems

Wireless technology has simplified networking by enabling multiple computer users to simultaneously share resources in an environment without the cumbersome and expensive process of deploying high-bandwidth wiring.  This technology supports end user roaming access to network facilities at comparable speeds of a conventional 10BaseT Ethernet network without the need to be tethered to a wall outlet.  Wireless networking has proven to be an easy way to deploy Ethernet connectivity in an un-cabled environment and with varying degrees of end user success.  Nonetheless, due to a variety of issues (e.g., poor performance, reliability, manageability, security, etc.), Architects should not arbitrarily assume wireless networking is a suitable replacement or substitute for high-bandwidth cabled connections.  Wireless shall be deployed only in those areas specifically designated by authorized UCSB IT, Planning, and Communications Services staff.

Furthermore, security in a wireless environment is a constant and evolving problem and therefore associated costs can be significant.  It is commonly understood that wireless networks are easier and cheaper to install than hard-wired networks, but when you factor in additionally needed and expensive wireless security applications and the personnel needed to manage them as well as the previously mentioned performance issues, wireless can - over time - cost more and under perform hard-wired networks.

Wireless networking standards or specifications were developed by the IEEE (Institute of Electrical and Electronic Engineers), which released the 802.11 specifications standard in 1999. All wireless networking products have been developed to comply with 802.11 specifications. Current IEEE standards support four subsets of the 802.11 standard. These subsets operate at different frequencies and data rate or throughput speeds, which are as follows:

- 802.11 – 2.4 Ghz frequency with throughput of 1 to 2 Mbps

- 802.11b – 2.4 GHz frequency with throughput up to 11 Mbps

- 802.11a – 5 GHz frequency with throughput up to 54 Mpbs

- 802.11g – 2.4 GHz frequency with throughput up to 54 Mbps (this standard offers faster data rates similar to 802.11a while maintaining compatibility with 802.11b.)

- 802.11n -  xxxxx

Wireless data rates or throughput are typically much less than standards stated rates and they tend to vary due to coverage distances a well as several other causes such as surrounding structures and RF interference, number of simultaneous users, and types (e.g., email vs. video streaming) of user sessions.

Examples of different standards and distance related data rates are as follows:

| LOCATION | STANDARD | FREQUENCY | DISTANCE | DATA RATE |
| --- | --- | --- | --- | --- |
| Indoor | 802.11b | 2.4 GHz | 150 Ft. | 11 Mbps |
| Indoor | 802.11b | 2.4 GHz | 350 Ft. | 1 Mbps |
| Outdoor | 802.11b | 2.4 GHz | 800 Ft. | 11 Mbps |
| Outdoor | 802.11b | 2.4 GHz | 2000 Ft. | 1 Mbps |
| Indoor | 802.11a/g | 5 GHz | 170 Ft. | 6 Mbps |
| Indoor | 802.11a/g | 5 GHz | 130 Ft. | 18 Mbps |
| Indoor | 802.11a/g | 5 GHz | 60 Ft. | 54 Mbps |
| Outdoor | 802.11a/g | 5 GHz | 1000 Ft. | 6 Mbps |
| Outdoor | 802.11a/g | 5 GHz | 100 Ft. | 54 Mbps |

For completeness this table should have information on 802.11n

Figure 4-7

Standards and Distance Related Data Rates

The 802.11 standard defines two operational modes, ad-hoc mode and infrastructure mode.  The ad-hoc mode is peer-to-peer, which involves two network devices (e.g., PC to PC, PC to Laptop, PC to printer, etc.) communicating with wireless network interface cards (NICs). The infrastructure mode involves multiple networked devices communicating with each other via an Access Point (AP).  In this scenario one or more APs act as base stations supporting multiple 802.11 enabled network devices with NICs in a defined geographic area. The AP is typically hardwired for data connectivity via Category 5E/6 cable and requires electrical power from conventional 110V or PoE (Power over Ethernet).  PoE utilizes unused pairs in Category 5E/6 cable to conduct low voltage power inserted at the cable origination point.  When designing spaces where wireless networking might be desired in the future, it is best to plan the AP densities and provide power and data drops near appropriate locations.

Infrastructure mode wireless networking, as described above, is a viable solution in an office or educational environment where fixed cabling to each network device is not practical or desired. When wireless network access is needed in public areas (indoors as well as outdoors), similar configurations using APs or Nodes, can support roaming internet, email and limited video streaming access.  This type of infrastructure situation is better known as a “Hotspot”.  A “Hotspot” requires additional software for provisioning/configuration, web-based management, security, billing, etc. This software typically resides on a dedicated device called a gateway or controller.

# Comments

bullets 1 and 2 seem to be redundantly specified as the deep double ganged box was already specified.

# Text boxes

Figure 4 – 1

Cable System Components